## Sheet1
Sl No. | Description | Compliance | Comments | Additional Comments 20220207 | Comments - Devashis Invendis | Comments - Shane 20220322 | Invendis Comments_Ravi | Business Case | Parameters to be considered | Logic
1 | TECHNICAL REQUIREMENTS
2 | Detailed System Requirements
3 | The system shall have or be able to perform the following:
8 | b) Display the value of network energy efficiency. | Compliant | How is data received | Tools are in place. Need business rules. Assume data coming from invendis api | API provides all energy data | dashboard/reports/mimics/nodered |  | This shall be the comparison of Energy Consumption across all sites in a business unit on Monthly basis comparison with present baseline (before implementation of Remote monitoring and control solution.) | Grid kWh, DG kWh, Battery kWh, Solar kWh of all sites | Total Monthly Energy (Site1 to Site n) Present Month/ Total Monthly Energy @ t0 | Total Monthly Energy = Σ(Grid kWh+DG kWh+Battery kWh+Solar kWh) (Site1 to Site n) | t0 = Baseline kWh for Site1 to Site n
9 | c) Display the proportions of (diesel/ alternative source) generator health status of healthy, sub-healthy and abnormal. | Compliant | How is data received | Tools are in place. Need business rules. Assume data coming from invendis api | API provides all monitoring parameters for Diesel Generator including fuel. | dashboard/reports/mimics/nodered |  | This has two logics. 1) Diesel generator kWh V/S Solar / Wind kWh for a given site. 2) Generator Health which shall be derived based on the above Ratio for applicable sites. | Applicable only for Alternate Power Source Driven Sites, selected site. Generator kWh, Solar kWh or Wind kWh. | Total Monthly Generator Energy kWh (Selected Site) / Total Monthly Solar / Wind Energy kWh (Selected Site) If above ratio > 0.85 then site health is healthy, 0.7 to 0.85 = sub-healthy, <0.7 abnormal. | Selected Site = Site of interest which user has selected.
10 | d) Display the proportions of battery health status of healthy, sub-healthy and abnormal. | Compliant | How is data received | Tools are in place. Need business rules. Assume data coming from invendis api | API provides data for rectifier and lithium battery. | dashboard/reports/mimics/nodered
36 | n) Human-computer interaction mode closed up troubleshooting experience base shall be supported, which means that maintenance engineers can share maintenance experience to other colleagues by sharing to remote monitoring system, then when the similar alarm occurred again, all the experience will be listed to maintenance engineer. | Compliant | tiKit Job Card system | tiKit Job Card system. its our commercialjobcard product which can integrate into systems via api. Need specification to implement. A monthly subscription is required for the service. If mtn takes an onsite commercial license we can discuss a sponsored license. tiKit runs on bitid servers. |  | Setup with Customer
37 | 3.1.2 Real-time Monitoring Requirements
38 | 1) Online Electronic Map navigation function:
39 | a) The system shall supports Online GIS (Geographic Information System, based on | Compliant | Google maps | Google maps |  | good
51 | 3) Entire network monitoring of site infrastructure energy efficiency and health status of battery: |  | dashboard/mimics/nodered | Tools are in place. dashboard/mimics/nodered. Need business rules to implement
52 | a) One-key to get the real-time value of Entire network site infrastructure energy efficiency, details of energy efficiency status, high efficiency or low efficiency, of each rectifiers for DC distribution. | Compliant | dashboard/mimics/nodered | Tools are in place. dashboard/mimics/nodered. Need business rules to implement |  | Just need the business rule to calculate this - LTME to supply |  | This is specific to sites with either rectifier is integrated with RMS and it provides data of AC Power V/S DC Power. Or This is applicable for sites with AC Energy and DC Energy Meters installed to monitor rectifier input and output power. Logic to be applied for all sites under this category. | AC KW Rectifier, DC KW Rectifier of Site 1 to Site n | DC KW / AC KW (Site 1 to Site n) If above ratio > 0.85 then site health is healthy, 0.7 to 0.85 = sub-healthy, <0.7 abnormal.
53 | b) One-key to get the ratio (%) of sub-healthy and abnormal battery, and state of health (healthy, sub-healthy and abnormal) of battery listed by sites. | Compliant | dashboard/mimics/nodered | Tools are in place. dashboard/mimics/nodered. Need business rules to implement |  | Just need the business rule to calculate this - LTME to supply
87 | 7) Efficient O&M Supporting Function
88 | 7.1 Battery management for the entire network
89 | a) The system shall provide not limited to the following overall network battery management function: | Compliant | How is data received | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  |  |  | Overall Battery Bank Voltage is part of parameters captured from site for legacy Lead Acid Batteries. For Li-Ion battery, SOC%, SOH% with DC Voltage shall be captured and provided for each Module in site. Aggregation of these parameters for each site and to all sites to be considered for this use case. |  | Individual Site Battery Health status to be displayed. This is part of Invendis RMS platform.
101 | 8) One-key analysis for rectifier and temperature control components:
102 | a) Displays temperature control losses and the expected value in a bar chart and renders dates on which the losses exceed the expected value. | Compliant | dashboard/mimics/nodered | Tools are in place. dashboard/mimics/nodered. Need business rules to implement |  | dashboard/reports/mimics/nodered |  | This is a site level information. Based on Temperature monitored in each site, thresholds defines over or under utilised cases of aircon. | Temperature of Shelter / Cabinet | Chart of expected temperature band V/S actual Band to be displayed with date on X-Axis. If actual temperature within the expected band, then the aircon is optimally utilised. If the deviation is towards lower end, then this is a case of over used and to be rectified by correcting the set temperature on Aircon. If deviation is towards higher end, then either settings in aircon to be verified and corrected or Aircon Cooling to be verified.
103 | b) Displays operating durations of air conditioners and the average rotational speed of fans in a bar chart and displays the environment temperature in a line chart. | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered | Rotational Speed of FAN cannot be captured in most of cases, hence it is not considered for logic building. | Aircon Usage Analysis, individual site. | Aircon Run Hours, Shelter Temperature, Ambient Temperature. | Chart as explained in requirement to be generated for each site.
104 | c) Analyses the temperature control losses, operating durations of air conditioners, environment temperature, and average rotational speed of fans. | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered |  | This is combination of above two use cases. No separate development to be considered for this.
105 | d) Analyses the historical hourly trends of ambient temperature, air conditioner uptime and average fan speed. | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered |  | Aircon Usage Analysis, individual site. | Ambient Temperature, Aircon Run Hour | Chart of Ambient temperature V/S Aircon Run Status to be plotted with time in X axis for each site
106 | e) Provides optimization suggestion and supports remote manual optimization. | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | Just need the business rule to calculate this - LTME to supply. AND what is remote manual optimization |  | Continuation of Use case in Sl No. 102.
107 | f) Displays the comparison results between PSU losses and the expected value in a bar chart and renders dates on which the losses exceed the expected value. | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered |  | This is specific to sites with either rectifier is integrated with RMS and it provides data of AC Power V/S DC Power. Or This is applicable for sites with AC Energy and DC Energy Meters installed to monitor rectifier input and output power. Logic to be applied for all sites under this category. | AC KW Rectifier, DC KW Rectifier of Site 1 to Site n | Chart of efficiency of PSU is plotted against the time in X-Axis for each site.
108 | g) Displays the real-time energy efficiency of power module. | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered |  | This is specific to sites with either rectifier is integrated with RMS and it provides data of AC Power V/S DC Power. Or This is applicable for sites with AC Energy and DC Energy Meters installed to monitor rectifier input and output power. Logic to be applied for all sites under this category. | AC KW Rectifier, DC KW Rectifier of Site 1 to Site n | PSU Efficiency to be displayed in user interface screen. This is a part of Invendis platform.
109 | h) Displays system load ratio in real-time. | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered |  | This is specific to sites with either rectifier is integrated with RMS and it provides data of DC Power and Module capacity. Or This is applicable for sites with DC Energy Meters installed to monitor rectifier output power and Manually entered Module Capacity. Logic to be applied for all sites under this category. | DC KW, Module Capacity in KW | DC KW / Module Capacity in KW. Value to be displayed in site dashboard.
110 | i) Analyzes the historical hourly trends of power module efficiency and system load ratio. | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered |  | Same as above | DC KW, Module Capacity in KW | Graph / Chart of Efficiency V/S Time in X Axis to be displayed.
111 | j) Provides optimization suggestion and supports remote manual optimization. | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | Just need the business rule to calculate this - LTME to supply. AND what is remote manual optimization |  | No. of Modules to be recommended or Battery Current Limit to be suggested to keep Module load under limit | DC KW, Module Capacity in KW | Display of No. of modules as per load, allow remote command to set Battery Current Limit. Remote command is part of Invendis platform.
131 | e) Customized indicator name management: Counter name can be redefined by customer, and redefined counter name can be batch applied to other sites. The indicator name can be recovered to default. | Compliant |  | Need more info but sure we can cater for it. |  | Need more info but sure we can cater for it. |  | Parameter Names to be configurable from a config matrix.
158 | 4 POWER MANAGEMENT TOOL (EMT) AND ENERGY UTILITY REPORTING SERVICE REQUIREMENTS
159 | 4.1 Introduction
160 | Most Opcos in MTN Group are currently unable to verify and reconcile the monthly, quarterly, bi-annually and annual received bills. This extends to the accuracy of the actual consumption of the various utility services. MTN must rely on the utilities’ quality, frequency and actual reading of billing statements to estimate annual budgets, energy, water, etc. Inaccurate energy data as well inefficient sources of energy and the dependency on fossil fuels such as diesel, produces a disaggregated and unsustainableGlobal Carbon footprint - reducing its emissions globally is a central drive across ournetwork. | Compliant | done
161 | 4.2 Scope details
162 | 4.2.1 Tool description/ Overview
163 | MTN faces growing consumer demand, 5G network capacity demand and ever less reliable grid (e.g. Eskom). MTN Group wishes to partner with an OEM to deliver smart asset management tools, produce actual cost-of-consumption reporting and optimize its energy mix and spend. | Compliant
164 | 4.2.2 Automated, Digitalized Solution and assist with Cost Reduction (Minimum scope requirement)
165 | Power management tool must be digitalized and automated solution with: | Compliant
166 | a) Autonomous management systems, Artificial Intelligence (AI) and machine learning, | Compliant | Need more info | Need more info | Most Opcos in MTN Group are currently unable to verify and reconcile the monthly, quarterly, bi-annually and annual received bills. This extends to the accuracy of the actual consumption of the various utility services. MTN must rely on the utilities’ quality, frequency and actual reading of billing statements to estimate annual budgets, energy, water, etc. Inaccurate energy data as well inefficient sources of energy and the dependency on fossil fuels such as diesel, produces a disaggregated and unsustainableGlobal Carbon footprint - reducing its emissions globally is a central drive across ournetwork. | This needs further discussion. We need direction as to what we apply AI to. We need to train a model based on business rules and then we can implement in the system |  | This is purely on the baselining and could be country specific logic / use case depending on the pain point of customer.
167 | b) Accurate measurement of energy consumption, | Compliant | done
168 | c) User friendly, plug and play functionality, | Compliant |  |  |  | dashboard/reports/mimics/nodered |  | This could be few widgets that can be added to the dashboard or removed based on need.
169 | d) Automated reporting where anomaly reporting should be prioritised based on the predetermined standard | Compliant | reporting tool | Alerting via email, various 3rd party such as trello, slack |  | dashboard/reports/mimics/nodered |  | Scheduled reports to be supported, where configured report will be sent over email at set time automatically.
170
171 | e) Real-time analytics, | Compliant |  | Tools are in place. dashboard/mimics/nodered. |  | dashboard/reports/mimics/nodered
172 | f) Billing control and functionality, | Compliant |  | Tools are in place. dashboard/mimics/nodered.
173 | g) Operational platform with per site view, with Housekeeping alarms integrated. | Compliant | Mimics/Online Scada | Tools are in place. dashboard/mimics/nodered. |  | dashboard/reports/mimics/nodered
174 | 4.2.3 Monitor and Report
175 | 1) The solution shall have ability to be configured to monitor and report each power and cooling equipment parameters such as: |  |  |  |  | dashboard/reports/mimics/nodered
176 | a) UPS – deployed capacity, input and output parameters such as V, A, P.F, KVA, KW,% Utilization | Compliant | done |  |  | dashboard/reports/mimics/nodered
177 | b) Rectifiers/batteries -deployed capacity, input and output parameters such as V, A, P.F, KVA, KW, % Utilization | Compliant |  |  |  | dashboard/reports/mimics/nodered
178 | c) HVAC – Relative humidity, Ambient temperature, return and supply temperatures, etc. | Compliant | how is data received | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api | Humidity & Temperature data is part of API. | dashboard/reports/mimics/nodered | Parameters will be captured and sent from RMS. This is part of Invendis solution
179 | d) Temperature readings – Actual temperature readings within a particular room | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered | Parameters will be captured and sent from RMS. This is part of Invendis solution
180 | e) Fuel levels/consumptions | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered | Fuel Level is captured using Fuel Sensor. This is part of Invendis solution
181 | f) Power Meter parameters that will show the followings per sites (total KVA, KW, P.F, % Loading, etc.) | Compliant | done |  |  | dashboard/reports/mimics/nodered
182 | 1) The ability of the solution to trend reports on each above depending on the period MTN want. | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered | Invendis platform has reports pertaining to above points.
183 | 2) Ability of the solution to trigger alarm if certain threshold is reached | Compliant | alerting | alerting | This is in Invendis scope | alerting
184 | 3) Ability to export trended reports in any format (graphic, excel, word, PDF, etc.). | Compliant |  | reporting |  | dashboard/reports/mimics/nodered
185 | 4) Ability of the solution to be integrated to existing MTN alarm platforms for 24 Hour alarm monitoring and handling . | Compliant | integration required | integration required. Need specification | This is in Invendis scope | okay so invendis handling? | Yes, Invendis will handle this.
186 | 5) To be configured to report PUE at every point requires (including the entire Data and switching centers, and per room in the data and switching centers). | Compliant |  | Tools are in place. dashboard/mimics/nodered. Need business rules to implement. Assume invendis api |  | dashboard/reports/mimics/nodered
187 | 4.2.4 Cost Reduction | Compliant
188 | Tool must also be able to assist with cost reduction (OPEX/ CAPEX savings): | Compliant | need more info | LTME | This is prediction algorithm that we believe is available in eSums.
189 | a) Reduce or eliminate fuel consumption, | Compliant |  | LTME |  | Is this invendis hardware requirement? | This will be addressed by Invendis hardware. However, an AI driven logic to be built in eSums that will understand the trend and set configuration in iSense hardware based on the site conditions.
190 | b) To enhance battery usage and lifespan, | Compliant |  | LTME |  | Is this invendis hardware requirement? | This will be addressed by Invendis hardware. However, an AI driven logic to be built in eSums that will understand the trend and set configuration in iSense hardware based on the site conditions.
191 | c) To identify and utilize the cheapest source of energy (grid, solar, batteries, etc) or optimise the energy mix to power our BTSs and DCs, | Compliant |  | LTME |  | Is this invendis hardware requirement? | This will be addressed by Invendis hardware. However, an AI driven logic to be built in eSums that will understand the trend and set configuration in iSense hardware based on the site conditions.
192 | d) Operational temperatures (-20°C to 60°C), | Compliant |  | need more info |  | Is this invendis hardware requirement? | This will be addressed by Invendis hardware. However, an AI driven logic to be built in eSums that will understand the trend and set configuration in iSense hardware based on the site conditions.
193 | e) Relative humidity of 85% non-condensing. | Compliant |  | need more info |  | Is this invendis hardware requirement? | This will be addressed by Invendis hardware.
194 | 4.2.5 Network Availability
195 | Lastly, OEM must design, supply and install an ecosystem that is able to monitor the impact on site availability and quality. The design should include a smart IoT energy tool ecosystem supported by algorithm to optimise the load and its associated Carbon footprint, in alignment with all available resources like, the weather bureau, Power Supplier (like Eskom in MTNSA) load shedding schedules etc. | Compliant | development. Need more info | Carbon Module. Additional development needed? If so specification needed | This is in Invendis scope | Invendis
196 | 4.2.6 Power platform details | Compliant
197 | The smart, self-learning platform must be remotely accessible and agnostic, allowing MTN Group to have a global aggregated view of its energy and Carbon footprint budget, across all its territories. The Dynamic Load Switching Power Tool platform should be highly automated, integrate to the existing MTN DC supply and support controlled ‘diesel’ genset usage, supported by proactive maintenance on the existing or future gensets. The OEM should provide the following off its cloud-based platform: | Compliant | integration required. need more clarity | development based on specification | MTN expects a central hosting solution, that aggregates data from various OPCO. | Need to discuss. Self-learning? | The self learning is referred to the AI driven logics of platform which predicts the modification of configurations in each of above use cases and sets the limits based on changing trends.
198 | a) Fully integrated billing stack, | Compliant | need more info | need more info | Billing system should be part of offering
199 | b) Billing grade OEM smart energy meter (Class 1 or better), | Compliant |  | LTME |  | Does sdg suppport this? | Invendis has proposed to supply the billing grade meters.
200 | c) Automated Pay As You Go Energy Meter reading and top-up functionality (MTN Group does not have the preferred vendor for this, | Compliant | need more info | sdg/LTME | Prepaid meter | Does sdg suppport this? | Invendis has proposed to supply the billing grade meters.
201 | d) Provisional billing functionality, | Compliant | done | Tools are in place. dashboard/mimics/nodered. |  | dashboard/reports/mimics/nodered
202 | e) Compare actual vs current costs from landlords or host MNOs, | Compliant |  | Tools are in place. dashboard/mimics/nodered. |  | dashboard/reports/mimics/nodered
203 | f) Universal tariff engine and tariff understanding, | Compliant | SA is loaded. Need tariffs for other areas
204 | g) Full integration into MTN’s financial backend, | Compliant | integration | Integration. specification required | Need to request MTN
205 | h) Consumption accounts fully automated to avoid disconnections, | Compliant | need more info | need more info | I believe, MTN expects an alert mechanism that tiggers when pre-paid meter is about to exhaust with currency. | Does sdg suppport this? | Refer inputs from Devashis
206 | i) Dispute handling between operator and the municipalities/utilities, | Compliant | LTME doing this? | LTME
207 | j) Monthly reporting that shows trends and give a clear view on exceptionally high and low usage anomalies | Compliant | dashboard/mimics/nodered | Tools are in place. dashboard/mimics/nodered. |  | dashboard/reports/mimics/nodered
210 | This IoT platform must be connected to the Weather Channel to predict solar or wind generation, automatically switches to the appropriate power source after checking availability and delivers continuous improvement across our infrastructure. | Compliant | integration | Integration. specification required |  | Integration. specification required | The solar prediction web service to be finalised to enable this integration.
211 | 4.2.7 Sustainability requirement
212 | An increase in energy costs, climate-related risks and regulation are pressurizing MTN to reduce energy use, cost and greenhouse gas (GHG) emissions. Investors are emanding climate-proofing by organisations, including MTN. Not only must MTN drive energy consumption, costs but GHG emissions which are growing faster than MTN’s revenue and subscribers | Compliant |  | This the carbon module |  | This the carbon module
222 | Our vision is to create and protect shared value for MTN and our stakeholders through responsible economic, environmental and social practices. The OEM energy platform should also produce individual or globally aggregated Sustainability Reports to MTN Group across all its territories at set frequency: | Compliant
223 | a) GHG Emission Software Tool & Carbon Management | Compliant | more info needed | carbon module | MTN expects Carbon footprint in a dashboard.
224 | b) Aggregate or individual CO2/sustainability reports – national/global | Compliant | more info needed | carbon module | Individual country specific and overall group specific carbon footprint in a dashboard.
225 | c) Apportion accurate carbon budget – landlords to TowerCos | Compliant | more info needed | carbon module
226 | d) Mitigate carbon tax implications | Compliant | more info needed | carbon module
227 | e) A live MTN carbon footprint dashboard | Compliant | dashboard/mimics/nodered | dashboard/mimics/nodered
228 | f) Interfacing between old EMS/ RMS and new EMT: vendor will have to confirm the interoperability of new system with existing ones in each OPCO and integrate with the existing NOC. What is the Type of connectivity from site to NOC/MTN management system – through SIM Card, wired or wireless? | Compliant | more info needed | more info needed | Invendis Scope
229 | g) Lastly, specify if there are any license renewal that apply or not in the vendor’s proposal. What is the mode of renewal if license applies? | Compliant | given to LTME | given to LTME